## Slide 1
Doing Things differently leads to something exceptional ……
WHAT IF WE CAN NOT HEAR IT, It is not there…
WHAT IF WE CANNOT SEE IT, it is not there…
This is what we have been taught since we were born….
INTEGRATED CONDITION MONITORING TECHNOLOGIES FOR ENERGY SAVING APPLICATIONS
TRANSTECH CONFERENCE
2018, PUNE

## Slide 2
Predictive maintenance
Costs are lower when we maintain only when a known need exists, what is the defect, how high, where and what spares and services to correct the defect.
GREEN SAILS SINGAPORE CONDITION MONITORING TECHNOLOGIES FOR MARINE, OFFSHORE AND INDUSTRY
The general idea behind Condition Monitoring:
Condition Based Monitoring or Machine Health Monitoring is to save cost, improve performance, prevent accidents, crew confidence & environment
Preventive maintenance
Costs are high when we maintain on schedule, Too often, disassembly and reassembly create damage.
Reactive maintenance
Costs are high-run machines until they fail and replace machines as needed.

## Slide 3
Condition monitoring or Integrating Vibration analysis with Ultrasound and Infrared thermography applications for Marine and off shore Industry
Three Proven Technologies
‘To Help & Keep Your machinery running’ with best results in-
- Economy,
- Prevent accidents and incidents,
- Improve operator confidence.
- Prevent environment pollution
TRANSTECH CONFERENCE
2018, PUNE
Notes: Humans are some what limited within our visual and audible ranges. We currently depend on our eyes and ears very heavily.
Infrared and ultrasound allows us to gather information from outside of those limited ranges. Information that is valuable in helping to determine well ahead of time that a piece of equipment, or one of its components, is beginning to fail.

## Slide 4
Lead times to failure offered by various conventional condition monitoring techniques
Courtesy web sources
TRANSTECH CONFERENCE
2018, PUNE

## Slide 5
Integrating Infrared with Ultrasound and Vibrations analysis applications for Marine and Off shore Industry
Courtesy web sources
TRANSTECH CONFERENCE
2018, PUNE

## Slide 6
BASIC understanding of vibration and component frequencies analysis
TRANSTECH CONFERENCE
2018, PUNE

## Slide 7
Vibrations of machinery
we basically compare today’s vibration spectrum (or “signature”) with other spectra obtained using the same instruments at the same locations last week, last month, or last year, or when the machine was first installed or immediately after an overhaul. We try to deduce internal changes (deterioration) from changes in the spectrum.

## Slide 8
A
M
P
L
ITUDE
FREQUENCY in Hz
FFT Spectrum in Velocity Vibration and the possible faults can identify from the spectrum
mm/s
TRANSTECH CONFERENCE
2018, PUNE

## Slide 9
FREQUENCY in Hz
A
M
P
L
ITUDE
Vibration analysis in Acceleration broadband spectrum
TRANSTECH CONFERENCE
2018, PUNE

## Slide 10
Time wave form – sample of random vibration
FFT spectrum of above wave form
TRANSTECH CONFERENCE
2018, PUNE

## Slide 11
Resonance occurs in a system when the frequency of a vibratory force (forcing frequency) is at or near a natural frequency.
Vibration levels at resonance are controlled through damping. Vibration amplification is determined by the proximity of the forcing frequency to natural frequency.
When high vibration is noted in rotating machinery, the analyst should conduct a thorough vibration analysis before applying commonly used resonance fixes. After all, excessive vibration could result from one or a combination of the following non-resonance situations:
1. pedestals, foundations, or structures
2. loose or missing bolts, broken welds, soft foot, or
3. mismatched parts excessive vibratory force
4. lack of damping.
Resonance
The Silent Killer of Rotating Machinery
TRANSTECH CONFERENCE
2018, PUNE

## Slide 12
SOLUTIONS FOR RESONANCE
To confirm the state of resonance in machinery, the analyst must verify the location of the system’s natural frequencies with a simple impact test, operating deflection shape, or modal test. The modal test will typically yield the most information.
Solutions
Reducing resonant-equipment vibration levels can involve any of the following actions, or a combination thereof:
Raising or lowering the natural frequency to distance it from the forcing frequency
2. Adding damping
3. Attaching an absorber.
TRANSTECH CONFERENCE
2018, PUNE

## Slide 13
4.0 K Hz – 01:15:24
6.35 Hz- 02:0.9:24
11.35 Hz- 03:31:36
TRANSTECH CONFERENCE
2018, PUNE

## Slide 14
1x
2x
3x
The overall vibration of this Boiler FD fan is showing 5.6396 mm/sec Vrms
2x and 3x is indicating order for misalignment of the motor and fan coupling
The higher order showing fairly good bearings and fan blades / impeller etc.,
Sample case study onboard ship
TRANSTECH CONFERENCE
2018, PUNE

## Slide 15
TRANSTECH CONFERENCE
2018, PUNE

## Slide 16
WHEN Resonance and Unbalance occur together with change in revolutions can cause serious damages
TRANSTECH CONFERENCE
2018, PUNE

## Slide 17
1:20:00 add Unbalance
TRANSTECH CONFERENCE
2018, PUNE

## Slide 18
MOTOR DE vibrations recorded as following-
1. Vertical - 8.953 mm/s RMS
2. Horizontal- 14.81 mm/s RMS
3. Axial- 7.2 mm/s RMS.
IACS limit for the Horizontal IG Motor is 7.0 mm/s RMS
Motor NDE side vibrations recorded as following-
1. Vertical - 10.75 mm/s RMS
2. Horizontal- 21.17mm/s RMS
3. Axial- 4.208 mm/s RMS.
IACS limit for horizontal IG fan is 7.0 mm/s RMS
TRANSTECH CONFERENCE
2018, PUNE

## Slide 19
High Vibrations caused by Misalignment case studies
TOO MANY SHIMS
TRANSTECH CONFERENCE
2018, PUNE

## Slide 20
High Vibrations caused by Misalignment case studies
Wrong shims and Improper fitting
TRANSTECH CONFERENCE
2018, PUNE

## Slide 21
High Vibrations caused by Misalignment case studies
TRANSTECH CONFERENCE
2018, PUNE

## Slide 22
High Vibrations caused by Misalignment case studies
TRANSTECH CONFERENCE
2018, PUNE

## Slide 23
High Vibrations caused by Misalignment case studies
Defective AV Mounts or resilient mountings shrunk
TRANSTECH CONFERENCE
2018, PUNE

## Slide 24
High Vibrations caused by Misalignment case studies
TRANSTECH CONFERENCE
2018, PUNE

## Slide 25
DEFECTIVE SHIMS

## Slide 26
Correct size and type shims increase the life of machinery with economical running.

## Slide 27
The ISO standards for the machinery vibration values limits
Courtesy web sources
TRANSTECH CONFERENCE
2018, PUNE

## Slide 28
VIBRATION MONITORING AND ANALYSIS IS LIKE SEEING THROUGH MACHINE
Courtesy web sources Mobius
TRANSTECH CONFERENCE
2018, PUNE

## Slide 29
Increase your Equipment Reliability with Ultrasound Technology

## Slide 30
What is Ultrasound?
Human range (16Hz to 18KHz)
Industry Applied range (20KHz to 100KHz) is Heterodyned for
Audible Human range
Diagnostic Ultrasound is for Medical Imaging
WELCOME
Energy Management with air borne ultra sound & structure borne ultra sound applications
Courtesy web sources
MARTECH CONFERENCE
2017 SINGAPORE

## Slide 31
Advantages of Ultrasound
Directional & Locatable
Useful in any Environments
Early Warning Failure Indication
Wide Range of Applications
Supports Other Technologies

## Slide 32
Applicable Ultra sound Inspections
Leak Detection
Electrical Inspection
Mechanical Inspection
Hydraulic components inspection
TRANSTECH CONFERENCE
2018, PUNE

## Slide 33: AIR/ GAS Compressor Valve Good n Bad
GOOD COMPRESSOR VALVE
LEAKING COMPRESSOR VALVE

## Slide 34
Typical LPG Valve with defective springs
Valve leak full in LPG compressor

## Slide 35
Normal Trap
Failed Open
Inverted Bucket Trap

## Slide 36
Air borne Ultrasound Electrical Inspection
Inspect enclosed systems while energized
Scan switchgear ‘before’ opening & inspect with infrared to
  Prevent ‘Arc Flash’ injury
  Sort equipment for further inspection
  Safety PPE for arc flash is very important for HV switch gear.
TRANSTECH CONFERENCE
2018, PUNE

## Slide 37: High Voltage PD condition
Corona
Only occurs at 1000V and above voltage.
This is a partial discharge(Leakage) activity.

## Slide 38: INSULATOR EARTH LEAK CONDITIONS
TRACKING
Tracking occurs where there is a low current pathway to ground across an insulator.
There is a build up and discharge of the voltage that produces “popping” sounds.
The discharge peaks correspond to the “popping” sounds.
They are not uniformly spaced in time.
TRANSTECH CONFERENCE
2018, PUNE

## Slide 39: Arc Flash Conditions
ARCING
Arcing, the discharge to ground is a high current pathway across an insulator.
This is a “burst of energy” that has a long duration discharge
TRANSTECH CONFERENCE
2018, PUNE

## Slide 40
  High Voltage Components are well enclosed, making for poor or sometimes impossible infrared inspection
BAD AND SEVERE TRACKING OF THE ELECTRICAL INSULATION

## Slide 41
TRACKING IN HIGH VOLTAGE INSULATORS
PD Tracking
TRANSTECH CONFERENCE
2018, PUNE

## Slide 42
Good Transformer

## Slide 43
TRANSFORMER WITH LOOSE WINDING

## Slide 44
Transformer with Tracking
MARTECH CONFERENCE
2017 SINGAPORE

## Slide 45: Ultrasound Mechanical Inspection
Slow Speed Bearings
Condition Based Lubrication
Historical Trending

## Slide 46
Very effective on Slow Speed Applications
Types of testing performed
  Comparison
  Historical Trending
  Spectrum Analysis
Bearing Inspection
Notes: Comparison between bearings of the same type in the same application, or over time as compared to baseline

## Slide 47
Good Bearing
Faulty Bearing
Receiving Lubrication
Bearing Testing

## Slide 48
One of the ship crane slewing operation defect identified in slewing motor counter balance valves
Ultra sound file

## Slide 49
Base on dB level
above baseline
Levels of Severity
With ultra sound
  8 dB Lubrication Required
  12 dB Minor Damage
  (microscopic faults)
  16 dB Damage (Visual faults)
  35+dB Failure Imminent

## Slide 50
Arcing: An electric discharge through normally non-conductive media such as air. It is a failure condition in electric equipment and can lead to fire or an explosion.
Corona: An electric discharge around conductors when the surrounding air is stressed beyond its ionization point without developing flashover.
FFT: Fast Fourier Transfer – A digital processing of a recorded signal representing data in terms of its component frequencies.
Tracking: Electricity follows a pathway to ground utilizing dirt and other contaminants until it reaches

## Slide 51: What is Infrared?
Infrared is a form of electromagnetic radiation
Everything above -273 oC (absolute zero) emits infrared radiation
The heat we feel from the sun is infrared energy
Notes: Bands of radiation
The scale shows the distance between the peaks of the waves. Different wave lengths represent different types of radiation.
TV will no longer be required on this chart with a few months
Long Wave

## Slide 52
Advantages of Infrared
Allows you to ‘see’ heat radiation
Non-invasive & safe to implement
Minimal downtime due to condition analysis electrical, mechanical and hydraulic problems
Effective prioritization of repairs to plan for spares, manpower and sub contractor selection etc.,
Improved employee safety and confidence of operators
Energy savings
Wide range of applications

## Slide 53: Increase machine Reliability with Infrared Technology
This could be catastrophic failure on a VLCC can cause fire in main switch board
Notes: This is an IR photo of a hydraulic room. (describe)

## Slide 54
The thermal image and related Digital image of Marine pump installation. In digital profile the pump and motor showing Good. In thermal image the motor is in trouble and drawing 10% excess amperes . The motor will burn if the action is not taken immediately.
This photo is taken in a leading company tanker vessel and displaying as example.
A TYPICAL MOTOR / PUMP PROBLEM - EXAMPLE

## Slide 55
A 250 kw motor inert gas fan in a vlcc operating with drive end bearing temperature of 93.3*c is going to cause damage to motor due to misalignment and overloading

## Slide 56
steam traps stuck (open) position:
waste of energy and damage to atmosphere condenser.($$$)
excess steam in system
create back pressure
back pressure can
cause other steam
traps to malfunction
steam trap stuck in shut (closed) position:
- water hammer
- line clog and corrode
- possible rupture
cause and effect of failed steam traps
DEFECTIVE STEAM TRAP

## Slide 57
A sample steam trap operating onboard steam turbine plant

## Slide 58: EXAMPLE OF MALFUNCTIONING OF PIPES, VALVES
The partially blocked pipe is an example of surface temperature effects in a pipe line

## Slide 59: COUPLINGS AND SHAFTS ALIGNMENT
Couplings inspection is difficult in normal operation.
We need to understand coupling, different coupling have different thermal signatures.
Misalignment, excessive wear are general defects are observed with infrared thermography.

## Slide 60
Sample evaporator liquid refrigerant inlet and expanded gas outlet at the return headers for each coil
Both above compressors connected to this defective evaporator coils. Loss of energy with 2 compressors running with minimum climate control effect

## Slide 61
A vacuum condenser operating at high temperature loss of vacuum and burning more fuel for additional steam demand causing losses of energy

## Slide 62
Main air compressor high pressure suction valves one valve is leaking badly other valve is chocked with carbon trouble- energy loss/ damage to valves, carbonisation in inter and after coolers and reduced efficiency

## Slide 63
The Gear box drive end bearing showing 85.4*C where the Lube oil temperature at the cooler inlet 48*c indicating trouble at the bearing condition.
Marine Propulsion Gear box showing high bearing temperatures

## Slide 64
A diesel generator alternator showing high temperatures can cause damages loss of alternator life due to excess temperatures

## Slide 65
Main start Air compressor onboard running very hot with LP discharge inlet to inter cooler about 194.2*C reduce the efficiency, long running hours and damage to many components like valves, coking in inter after coolers etc.,

## Slide 67: Hydraulic applications
Leaking hydraulic system valves
Clogged filters
Moisture and contamination in hydraulic oil
Hot hydraulic motors, pumps condensers etc.,

## Slide 68
Pumps and hydraulics
A blocked filter top side hot oil flowing, bottom side cooler and showing no oil flow(blockage) through filter.
A good filter IN A CRANE HYDRAUIC SYSTEM

## Slide 69
A windlass hydraulic pump during heaving anchor operation

## Slide 70
Ultrasound, Thermography and Vibration analysis combined survey
Ultrasound (US) – Ultra sound signature - Hear the sound radiation what we cannot hear
Thermography (IR) – Thermal signature- See the infrared radiation what we cannot see.
Vibration Survey (VS) - Vibration signature- The physical movement of machine language speaking about the condition.
Integration of US,IR and VS will produce a better integrated survey findings and diagnosis result

## Slide 72
Thanks for your kind
Attention
Green sails Singapore contributing for energy savings and thanks to TRANSTECH CONFERENCE ORGANISERS TOLANI MARITIME INSTITUTE, PUNE 2018.
Welcomes your
Questions
Comments n
Suggestions